|  |  |  |
| --- | --- | --- |
|  | SAN DIEGO AIR POLLUTION CONTROL DISTRICT**COMPLIANCE DIVISION**10124 Old Grove RoadSAN DIEGO CA 92131-1649PHONE (858) 586-2650 FAX (858) 586-2651 | *APCD USE ONLY* |
| SECTOR |
| ID# |
| NOV# |

VP1000/DISPENSER INTEGRITY TEST

Exhibit 14 & IOM of VR 201/202

**Facility Name:**       **A/C or PO Number:**       **Time of Test:**

 (Record exact time of test in order to demonstrate proper test sequencing as required in Attachment A)

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
|  **Dispenser No.** | Exhibit 14 & IOM B-3 | Exhibit 14 & IOM B-4 | IOM B-5 | IOM B-6 |
| Vacuum ReadingInitial1(WC) | Vacuum ReadingAfter closingthe ball valve1(WC) | Vacuum ReadingAfter 60 sec.2(WC) | Dispenser Side | Dispensing Vacuum3(WC) | Change in Speed(check one) |
|       |       |       |       | A |       | [ ]  YES [ ]  NO |
| B |       |
|       |       |       |       | A |       | [ ]  YES [ ]  NO |
| B |       |
|       |       |       |       | A |       | [ ]  YES [ ]  NO |
| B |       |
|       |       |       |       | A |       | [ ]  YES [ ]  NO |
| B |       |
|       |       |       |       | A |       | [ ]  YES [ ]  NO |
| B |       |
|       |       |       |       | A |       | [ ]  YES [ ]  NO |
| B |       |
|       |       |       |       | A |       | [ ]  YES [ ]  NO |
| B |       |
|       |       |       |       | A |       | [ ]  YES [ ]  NO |
| B |       |

1 These vacuum readings shall be at least 60” Water Column (WC)

2 Final vacuum reading shall not fall more than 4” WC from the reading taken after closing the ball valve.

3 The dispensing vacuum shall not be less than 60” WC