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[bookmark: Exhibit_10_of_ARB_E.O._VR_203-X_or_VR-20]VAPOR PRESSURE SENSOR VERIFICATION TEST PROCEDURE
Exhibit 10 of ARB E.O. VR 203-X or VR-204-X
☐ Renewal Testing
☐ Compliance Witness
☐ Compliance Testing
☐ Engineering Evaluation
(Contractor only)
(District only)
(District only)




Facility Name:		A/C or PO Number:		Time of Test:	
(Record exact time of test in order to demonstrate proper test sequencing as required in Attachment L)
	PRESSURE SENSOR INFORMATION

	Pressure Sensor Location:
Dispenser No.: 	/	
	Pressure Sensor Serial No. 	



	FACILITY AND TESTING EQUIPMENT INFORMATION

	Date and Time of Last Fuel Delivery:
	

	Processor Status During Test: (Applicable for VST membrane processor only)
	☐ ON	☐ OFF

	Calibration Date of Digital Manometer:
	



	UST PRESSURE REFERENCE CHECK

	UST Pressure from Digital Manometer1
		 Inches of W.C.

	Vapor Containment Area Pressure1
(Obtain Value from TLS Console using Figure 8-4)
		 Inches of W.C.

	Difference in Pressure Readings1,2
		 Inches of W.C.

	Is the difference in pressure readings between ± 0.20” W.C.?
	☐ YES	☐ NO

	Once test completed was the Mode Key pressed to exit the PMC/ISD Diagnostic Menu?
	☐ YES



	AMBIENT REFERENCE CHECK

	Was the Reference Port Cap removed?
	☐ YES

	Was the pressure sensor valve set to the Ambient Reference Port?
(Refer to Figure 8.3)
	☐ YES

	Vapor Containment Area Pressure1
(Obtain Value from TLS Console using Figure 8-4)
		 Inches of W.C.

	Is the sensor pressure value between ± 0.20” W.C.?
	☐ YES	☐ NO

	Was the Reference Port Cap replaced?
	☐ YES

	Once test completed was the Mode Key pressed to exit the PMC/ISD Diagnostic Menu?
	☐ YES



1 Record the pressure in inches of water column (W.C.), to the nearest hundredth.
2 Difference in Pressure Readings = UST Pressure from Digital Manometer – Vapor Containment Area Pressure, in inches of W.C., to the nearest hundredth. (Only applicable for the UST Pressure Reference Check)
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