| SAN DIEGO AIR POLLUTION CONTROL DISTRICT COMPLIANCE DIVISION 10124 OLD GROVE ROAD SAN DIEGO CA 92131 PHONE (858) 586-2650 | APCD USE ONLY |
| --- | --- |
|  | SECTOR |
|  | ID# |
|  | NOV# |

# VEEDER-ROOT VAPOR POLISHER OPERABILITY TEST PROCEDURE

For ISD Alarm Response Purposes only: Processor ball valves in proper orientation, processor is in the on and automatic vapor processor mode and nozzle boots inspected for damage :Yes	No

Exhibit 11 of ARB E.O. VR 203-X or VR-204-X

Facility Name:	A/C or PO Number:	Date/Time of Test:

| FACILITY AND TEST EQUIPMENT INFORMATION |  |
| --- | --- |
| Date and Time of Last Vapor Polisher Load or Purge: |  |
| Date and Time of Last Fuel Delivery: |  |
| Calibration Date of Flow Meter: |  |
| Calibration Date of Electronic Pressure Measuring Device: |  |
| Calibration Date of Thermometer: |  |

| PRESSURE INTEGRITY TEST RESULTS |  |  |
| --- | --- | --- |
| Date and Time the Vapor Valve was closed: |  |  |
| Vapor Control Valve Manually Closed?1 |  | ☐ YES ☐ NO |
| 3-Way Ball Valve in Correct Testing Position? Refer to Figure 1 |  | ☐ YES ☐ NO |
| Leak Detection Solution used during pressure integrity test to check for leaks at the compression fittings found at the bottom of the Vapor Polisher? |  | ☐ YES ☐ NO |
|  | Initial Test | Retest (If Applicable) ☐ N/A |
| Initial Pressure Reading | inches W.C. | inches W.C. |
| Start Pressure Reading [After 1 minute (60 seconds)]2 | inches W.C. | inches W.C. |
| Final Pressure Reading [After 2 minutes (120 seconds)]2 | inches W.C. | inches W.C. |
| Difference in Start & Final Pressure Readings | inches W.C. | inches W.C. |
| Final Pressure Greater than 7.0 inches W.C.? | ☐ YES ☐ NO | ☐ YES ☐ NO |
| Final Pressure Greater than Start Pressure? | ☐ YES ☐ NO | ☐ YES ☐ NO |
| If No, is the Decrease in Pressure less than 0.5 inches W.C.? | ☐ YES ☐ NO | ☐ YES ☐ NO |
| RESULTS: PASS/FAIL |  |  |

| FLOW TEST RESULTS |  |
| --- | --- |
| Vapor Control Valve Manually Opened?3 | ☐ YES ☐ NO |
| Flow Rate4 | SCFH |
| Pressure Reading at Inlet2 | inches W.C. |
| Is the Pressure Reading between 1.69 and 2.25 inches W.C.? | ☐ YES ☐ NO |
| Vapor Valve in Automatic Mode after completing Flow Test?5 | ☐ YES ☐ NO |
| Inlet Test Port in Normal Operating Position after completing Flow Test? | ☐ YES ☐ NO |
| RESULTS: PASS/FAIL |  |

| THERMOMETER TEST RESULTS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| VAPOR VALVE THERMOMETER |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Ambient Temperature6 (°F) |  | Outlet Temperature7 (°F) |  |  | Calibrated Thermometer Reading (°F) |  | Difference in Temperatures7 (°F) |  | Pass/ Fail |  |
| ☐ Initial Test Only |  | Initial Test Results |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Re-test Results ☐ N/A |  | Introduced Nitrogen into Canister for 2 minutes prior to printing Temperature Diagnostic Report? ☐ YES ☐ NO |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Additional Test Results ☐ N/A |  | Removed Outlet Temperature Probe from the Canister & waited at least 15 minutes prior to comparing temperatures? ☐ YES ☐ NO |  |  |  |  |  |  |  |  |  |  |  |  |  |
| GASOLINE UST TANK THERMOMETER |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Product Grade of the Gasoline Storage Tank | Gasoline Tank Thermometer Values |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Initial Test Results |  |  |  |  | Additional Test Results |  |  |  |  |  |  |  |  |  |
|  | T58 (°F) |  | T410 (°F) | Difference in Temperatures (T5-T4) (°F) |  | Removed tank probe & waited at least 15 minutes prior to comparing temperatures? |  |  | T510 (°F) |  | Calibrated Thermometer Reading (Cal)10 (°F) |  | Difference in Temperatures (T5-Cal) (°F) |  | Pass/ Fail |
|  |  |  |  |  |  | ☐ YES |  | ☐ NO |  |  |  |  |  |  |  |
|  |  |  |  |  |  | ☐ YES |  | ☐ NO |  |  |  |  |  |  |  |
|  |  |  |  |  |  | ☐ YES |  | ☐ NO |  |  |  |  |  |  |  |
|  |  |  |  |  |  | ☐ YES |  | ☐ NO |  |  |  |  |  |  |  |
|  |  |  |  |  |  | ☐ YES |  | ☐ NO |  |  |  |  |  |  |  |

| ATMOSPHERIC PRESSURE SENSOR TEST RESULTS |  |
| --- | --- |
| Atmospheric Pressure Reading from TLS Console9 | PSI |
|  | inches Hg |
| Atmospheric Pressure Reading from a Local Independent Source | inches Hg |
| Difference in Pressure Reading Between Local Source and TLS Console10 | inches Hg |
| Value for 10% of Local Source11 | inches Hg |
| Difference between Local Source and TLS Pressure Reading less than 10% of Local Source? | ☐ YES ☐ NO |
| RESULTS: PASS/FAIL |  |

1 Attach the IV8000 RS232 Command Report to this test result form indicating the date and time the valve was last closed automatically as well as the date and time the valve was manually closed.

2 Record the pressure reading, in inches water column (W.C.), to the nearest hundredth (e.g. 0.01 inches W.C.).

3 Attach the IV8000 RS232 Command Report to this test result form indicating the date and time the valve was manually opened.

4 Record the flow rate, in standard cubic feet per hour (SCFH), to the nearest tenth (e.g. 0.1 SCFH).

5 If the Hydrocarbon Verification Test per Exhibit 12 of VR-203-X/VR-204-X will be performed after this test, then the ball valve can be closed after the hydrocarbon verification test has been completed.

6 Attach the Vapor Valve Diagnostic Report(s) from the TLS Console to this test result form indicating the Vapor Polisher Ambient and Outlet Temperatures.

7 Difference in Temperatures = │Ambient Temperature – Outlet Temperature│ or vice versa.

8 Attach the In-Tank Diagnostic Report(s) from the TLS Console to this test result form for each gasoline tank tested indicating the T4 and T5 temperature values.

9 Attach the ATMP Sensor Smartsensor Diagnostic Report to this test result form indicating the atmospheric pressure, in pounds per square inch (PSI). To convert the pressure from PSI (PPSI) to inches Hg (inches Mercury, PHg), use the following equation:

PHg  (PPSI  14.7) * 2.036

10 Difference in Pressure Reading = │TLS Console Pressure Reading – Local Source Pressure Reading│ or vice versa, inches Hg.

11 Value for 10% of Local Source = 0.10 * Pressure Reading from Local Source, inches Hg.