APCD USE ONLY

SECTOR

ID#

NOV#

SAN DIEGO AIR POLLUTION CONTROL DISTRICT

COMPLIANCE DIVISION 10124 OLD GROVE ROAD SAN DIEGO CA 92131-1649 PHONE (858) 586-2650

For ISD Alarm Response Purposes only: Nozzle Boots Inspected for Damage: ☐ Yes	☐ No

LIQUID REMOVAL

## Exhibit 5 of VR-203-XX and VR-204-XX / TP 201.6C (Option One/Short Version)

Facility Name:		A/C or PO Number:		Time of Test:

(Record exact time of test in order to demonstrate proper test sequencing as required in Attachment L)

| (Number of nozzles x grades per nozzle) Total grade points onsite: | [A] Grade points not tested due to low flowrate (<6.0 gpm): | [C] Grade points not tested for any other reason (eg. Defects): | # of grade points LR tested that passed: |
| --- | --- | --- | --- |
| Pre-Inspection1: Hoses in compliance? ☐ YES ☐ NO | [B] Grade points not tested due to high flowrate (>10.0 gpm): | Total number of Fueling Points LR tested (excluding boxes [A],[B],&[C]): | # of grade points LR tested that failed: |

| Fueling Point & Grade (87/89/91) | Hose Make & Model | Gallons Dispense d (gal) (G)2 | Time to Dispense (sec) (T)2 | Screening Dispensing Rate (gal/min)2 | Existing volume drained from hose (mls) | Volume added to hose (mls) 150- 175(VI)3 | Gallons Dispensed6 (7 +/-0.5 gal) (G) 3,4 | Time to Dispense (sec) (T)4 | Test Dispensing Rate (gal/min)3, 4 | Volume Drained After Dispensing (mL) (VF) 3,4 | Liquid Removal Rate (mL/gal) 3,4,5 | Pass (P) or Fail (F) or Non-Test (NT) | Comments |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

## Exhibit 5 of VR-203-X and VR-204-X Option 1 (short version)

Facility Name:		A/C or PO Number:		Time of Test:

(Record exact time of test in order to demonstrate proper test sequencing as required in Attachment L)

| Fueling Point & Grade (87/89/91) | Hose Make & Model | Gallons Dispensed2 (gal) (G) | Time to Dispense2 (sec) (T) | Screening Dispensing Rate (gal/min)2 | Existing volume drained from hose (mls) | Volume added to hose (mls) 150- 175(VI)3 | Gallons Dispensed (7 +/-0.5 gal) (G) 3,4 | Time to Dispense (sec) (T)3,4 | Test Dispensing Rate (gal/min)3,4 | Volume Drained After Dispensing (mL) (VF) 3,4 | Liquid Removal Rate (mL/gal) 3,4,5 | Pass (P) or Fail (F) or Non-Test (NT) | Comments |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

- Inspect hoses for slits, tears and any Title 17 defects for hanging hardware specified in Exhibit 2 of VR-203-XX or VR-204-XX. Replace defective hoses prior to proceeding with the test.

- The flow rates for all grade points must be tested and verified to be within the range of 6.0-10.0 gallons per minute (gpm). A minimum of one gallon of gasoline must be dispensed when measuring initial flowrates. If the flowrate is determined to be outside of 6.0-10.0 gpm during the initial flow rate screening, the flow rate of the given grade point must be re-tested by timing for a minimum of 30 seconds. The liquid removal test shall not be conducted for any hose with a grade point that measured outside of 6.0-10.0gpm range.

- Entry fields applicable only if existing gasoline drained from the vapor hose is equal to or greater than 25 milliliters

- If the existing gasoline drained from the vapor hose is equal to or greater than 25 milliliters, then a liquid removal test must be conducted per Option One of Exb.5. After 150-175 ml’s of gasoline is added to the vapor path, 7.0 +/- 0.5 gallons must be dispensed at a flow rate within 6.0-10.0 gpm.

- If the liquid removal rate is less than 5.0 ml/gallon, but greater than or equal to 4.5 ml/gallon, repeat the test two additional times and average the three results.